## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Electricity Invercargill Limited
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Electricity Invercargill Limited
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | 94236-94236 | 113/2 Lewis E Of Dee (2) | ELIN | Leven St 12 LEV 12 | 2024-04-08 | 23:04 | 2024-04-08 | 23:10 | 0.014897 | 0.0024828 | 44 | 6 | Planned | Planned interruption | Upgrade - Cable testing
10 |  | 94083-94083 | 371/3 Tay W Of Stuart (3) | ELIN | Racecourse Rd 8 RRD 8 | 2024-04-09 | 9:32 | 2024-04-09 | 13:22 | 0.012978 | 5.6427e-05 | 1 | 230 | Unplanned | Other cause | Upgrade - Safety isolation - LV Board alterations & New LV fuse installation
11 |  | 94139-94139 | Spey St 8 | ELIN | Spey St 8 SPY 8 | 2024-04-16 | 8:00 | 2024-04-16 | 14:51 | 2.4583 | 0.0059813 | 106 | 411 | Planned | Planned interruption | Ring main unit maintenance - Service Ring main unit
12 |  | 94300-94300 | 869/1 Forfar Cres Reserve | ELIN | Racecourse Rd 6 RRD 6 | 2024-05-07 | 8:31 | 2024-05-07 | 14:00 | 1.0025 | 0.0030471 | 54 | 329 | Planned | Planned interruption | Upgrade - Replace Transformer LV board
13 |  | 94303-94303 | 358/2 Inglewood N Of Otepuni (2) | ELIN | Southern 8 SOU 8 | 2024-05-07 | 8:54 | 2024-05-07 | 11:09 | 1.2874 | 0.0095362 | 169 | 135 | Planned | Planned interruption | Upgrade - Ring main unit maintenance
14 |  | 94317-94317 | 357/4 Otepuni At Lindisfarne (4) | ELIN | Southern 9 SOU 9 | 2024-05-08 | 19:31 | 2024-05-09 | 3:01 | 0.50784 | 0.0011285 | 20 | 450 | Planned | Planned interruption | Upgrade - Ring main unit maintnenace
15 |  | 94317-94318 | 835/2 Prospect W Of Inglewood | ELIN | Southern 8 SOU 8 | 2024-05-08 | 19:32 | 2024-05-09 | 3:04 | 0.58662 | 0.0012978 | 23 | 452 | Planned | Planned interruption | Upgrade - Replace poles & wires
16 |  | 94334-94334 | 533/2 Tay E Of Jed | ELIN | Spey St 14 SPY 14 | 2024-05-12 | 23:00 | 2024-05-13 | 3:16 | 0.30335 | 0.001185 | 21 | 256 | Planned | Planned interruption | Upgrade - Ring main unit maintenance
17 |  | 94469-94469 | Leven St 11 | ELIN | Leven St 11 LEV 11 | 2024-05-22 | 9:21 | 2024-05-22 | 11:52 | 0.0085205 | 5.6427e-05 | 1 | 151 | Unplanned | Other cause | Upgrade - Remove transformer
18 |  | 94567-94567 | 305/3 Yarrow W Of Adamson Cres East | ELIN | Spey St 11 SPY 11 | 2024-06-05 | 8:02 | 2024-06-05 | 13:45 | 1.4129 | 0.0041192 | 73 | 343 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance
19 |  | 94567-94567 | 305/4 Yarrow W Of Adamson Cres East | ELIN | Spey St 11 SPY 11 | 2024-06-05 | 8:02 | 2024-06-05 | 13:50 | 1.9833 | 0.0056991 | 101 | 348 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance
20 |  | 94602-94602 | 320/3 Yarrow Opp Lithgow St (3) | ELIN | Racecourse Rd 8 RRD 8 | 2024-06-09 | 7:00 | 2024-06-09 | 9:46 | 0.51518 | 0.0031035 | 55 | 166 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance
21 |  | 94631-94631 | 445/2 Bute St (2) | ELIN | Leven St 13 LEV 13 | 2024-06-12 | 20:00 | 2024-06-13 | 0:36 | 0.59181 | 0.0021442 | 38 | 276 | Planned | Planned interruption | Upgrade - Remove redundant transformer
22 |  | 94689-94689 | 358/2 Inglewood N Of Otepuni (2) | ELIN | Southern 8 SOU 8 | 2024-06-18 | 8:23 | 2024-06-18 | 14:53 | 3.7411 | 0.0095926 | 170 | 390 | Planned | Planned interruption | Serive ring main unit - Ring main unit maintenance
23 |  | 94704-94704 | Do 123951 | ELIN | Ocean Beach BFE 2 | 2024-06-19 | 8:09 | 2024-06-19 | 15:30 | 0.84607 | 0.0019185 | 34 | 441 | Planned | Planned interruption | New connection - New transformer
24 |  | 94706-94706 | Leven St 7 | ELIN | Leven St 7 LEV 7 | 2024-06-19 | 17:53 | 2024-06-19 | 21:37 | 0.050559 | 0.00022571 | 4 | 224 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance
25 |  | 94731-94731 | 501/2 Kmart Forth St (2) | ELIN | Spey St 9 SPY 9 | 2024-06-23 | 7:32 | 2024-06-23 | 10:53 | 0.056709 | 0.00028214 | 5 | 201 | Planned | Planned interruption | Service ring main unit - Ring main unit mainteance
26 |  | 94742-94742 | 250/2 Earn East Of Conon(2) | ELIN | Leven St 11 LEV 11 | 2024-06-25 | 8:17 | 2024-06-25 | 11:32 | 0.92427 | 0.0047399 | 84 | 195 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance
27 |  | 94750-94750 | 967 Liffey S. Of Bann | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 11:16 | 0.35944 | 0.0039499 | 70 | 91 | Unplanned | Unknown | Unknown - CB Tripped
28 |  | 94750-94750 | Shannon St S Of Gore St | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 11:00 | 0.84641 | 0.011285 | 200 | 75 | Unplanned | Unknown | Unknown - CB Tripped
29 |  | 94750-94750 | Bann St Cb Bann St Cb | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 9:53 | 0.16522 | 0.020652 | 366 | 8 | Unplanned | Unknown | Unknown - CB Tripped
30 |  | 94750-94750 | 962 Bann E Of Liffey 962 | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 11:27 | 0.65613 | 0.0064327 | 114 | 102 | Unplanned | Unknown | Unknown - CB Tripped
31 |  | 94750-94750 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 10:45 | 0.074484 | 0.0012414 | 22 | 60 | Unplanned | Unknown | Unknown - CB Tripped
32 |  | 94750-94750 | 961 Bann W Of Liffey | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 11:14 | 0.14564 | 0.0016364 | 29 | 89 | Unplanned | Unknown | Unknown - CB Tripped
33 |  | 94750-94750 | 929/1 Suir N Of Ocean Beach Rd (1) | ELIN | Bluff Borough BFE 1 | 2024-06-26 | 9:45 | 2024-06-26 | 9:55 | 0.030471 | 0.0030471 | 54 | 10 | Unplanned | Unknown | Unknown - CB Tripped
34 |  | 94768-94768 | 929/1 Suir N Of Ocean Beach Rd (1) | ELIN | Bluff Borough BFE 1 | 2024-06-27 | 18:32 | 2024-06-27 | 18:47 | 0.046552 | 0.0031035 | 55 | 15 | Unplanned | Defective equipment | Deterioration - Failed insulator
35 |  | 94768-94768 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2024-06-27 | 18:32 | 2024-06-27 | 22:13 | 0.28682 | 0.0012978 | 23 | 221 | Unplanned | Defective equipment | Deterioration - Failed insulator
36 |  | 94768-94768 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2024-06-27 | 18:32 | 2024-06-27 | 19:52 | 0.099312 | 0.0012414 | 22 | 80 | Unplanned | Defective equipment | Deterioration - Failed insulator
37 |  | 94768-94768 | 961 Bann W Of Liffey | ELIN | Bluff Borough BFE 1 | 2024-06-27 | 18:32 | 2024-06-27 | 20:20 | 1.2798 | 0.01185 | 210 | 108 | Unplanned | Defective equipment | Deterioration - Failed insulator
38 |  | 94768-94768 | Shannon St S Of Gore St | ELIN | Bluff Borough BFE 1 | 2024-06-27 | 18:32 | 2024-06-27 | 20:54 | 1.3942 | 0.0098183 | 174 | 142 | Unplanned | Defective equipment | Deterioration - Failed insulator
39 |  | 94768-94768 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2024-06-27 | 20:17 | 2024-06-27 | 20:19 | 0.0024828 | 0.0012414 | 22 | 2 | Unplanned | Defective equipment | Deterioration - Failed insulator
40 |  | 94805-94805 | 490/2 Pumping Stn, Stead St (2) | ELIN | Leven St 13 LEV 13 | 2024-07-01 | 8:15 | 2024-07-04 | 9:40 | 0.74568 | 0.00016928 | 3 | 4405 | Unplanned | Other cause | New connection - Relocate RMU & transformer
41 |  | 94805-94805 | 490/2 Pumping Stn, Stead St (2) | ELIN | Leven St 13 LEV 13 | 2024-07-04 | 7:43 | 2024-07-04 | 9:40 | 0.019806 | 0.00016928 | 3 | 117 | Unplanned | Other cause | New connection - Relocate RMU & transformer
42 |  | 94810-94810 | 266/4 Eye W Of Nith (4) | ELIN | Spey St 9 SPY 9 | 2024-07-04 | 9:20 | 2024-07-04 | 13:22 | 0.040966 | 0.00016928 | 3 | 242 | Unplanned | Defective equipment | Deterioration - Failed transformer
43 |  | 94810-94810 | 266/3 Eye W Of Nith (3) | ELIN | Spey St 9 SPY 9 | 2024-07-04 | 12:39 | 2024-07-04 | 12:48 | 0.026916 | 0.0029906 | 53 | 9 | Unplanned | Defective equipment | Deterioration - Failed transformer
44 |  | 94838-94838 | 163/3 Ramrig N Of Lewis (3) | ELIN | Spey St 10 SPY 10 | 2024-07-09 | 8:12 | 2024-07-09 | 11:10 | 0.5022 | 0.0028214 | 50 | 178 | Planned | Planned interruption | Upgrade - RMU maintenance
45 |  | 94843-94843 | 642/3 Salford S Of Lamond | ELIN | Racecourse Rd 12 RRD 12 | 2024-07-09 | 8:22 | 2024-07-09 | 14:51 | 2.4145 | 0.006207 | 110 | 389 | Planned | Planned interruption | Upgrade - RMU maintenance
46 |  | 94838-94838 | 163/4 Ramrig N Of Lewis (4) | ELIN | Spey St 10 SPY 10 | 2024-07-09 | 8:28 | 2024-07-09 | 11:15 | 0.0094233 | 5.6427e-05 | 1 | 167 | Planned | Planned interruption | Upgrade - RMU maintenance
47 |  | 95197-95197 | Leven St 13 | ELIN | Leven St 13 LEV 13 | 2024-08-20 | 10:27 | 2024-08-20 | 11:02 | 0.38511 | 0.011003 | 195 | 35 | Unplanned | Third party interference | Third party vehicle - Broken pole
48 |  | 95197-95197 | 405 Mersey N. Of Bond Pl. | ELIN | Leven St 13 LEV 13 | 2024-08-20 | 10:27 | 2024-08-20 | 15:19 | 0.2142 | 0.00073355 | 13 | 292 | Unplanned | Third party interference | Third party vehicle - Broken pole
49 |  | 95248-95248 | Do 16025 | ELIN | Ocean Beach BFE 2 | 2024-08-26 | 20:34 | 2024-08-27 | 5:05 | 0.086503 | 0.00016928 | 3 | 511 | Planned | Planned interruption | Upgrade - Install earthing points
50 |  | 95248-95248 | 973 Foreshore Rd | ELIN | Ocean Beach BFE 2 | 2024-08-26 | 20:34 | 2024-08-26 | 22:34 | 0.27085 | 0.0022571 | 40 | 120 | Planned | Planned interruption | Upgrade - Install earthing points
51 |  | 95292-95292 | 404 Bond Pl. W. Of Mersey (404). | ELIN | Leven St 13 LEV 13 | 2024-09-01 | 8:31 | 2024-09-01 | 10:09 | 0.094007 | 0.00095926 | 17 | 98 | Planned | Planned interruption | Upgrade - Repair switch
52 |  | 95292-95292 | 436 Mersey At Spey | ELIN | Leven St 13 LEV 13 | 2024-09-01 | 8:35 | 2024-09-01 | 10:14 | 0.055863 | 0.00056427 | 10 | 99 | Planned | Planned interruption | Upgrade - Repair switch
53 |  | 95344-95344 | Leven St 9 | ELIN | Leven St 9 LEV 9 | 2024-09-03 | 15:00 | 2024-09-03 | 18:57 | 0.013373 | 5.6427e-05 | 1 | 237 | Planned | Planned interruption | Fleet plan - Transformer maintenance
54 |  | 95344-95344 | 431/1 Sth Construction Co Bond St | ELIN | Leven St 9 LEV 9 | 2024-09-03 | 15:03 | 2024-09-03 | 18:57 | 0.026408 | 0.00011285 | 2 | 234 | Planned | Planned interruption | Fleet plan - Transformer maintenance
55 |  | 95409-95409 | Do 14529 | ELIN | Bluff Borough BFE 1 | 2024-09-07 | 11:31 | 2024-09-07 | 12:09 | 0.038596 | 0.0010157 | 18 | 38 | Unplanned | Defective equipment | Deterioration - Failed lead
56 |  | 95481-95481 | 685/1 Bourke E Of Windsor | ELIN | Spey St 11 SPY 11 | 2024-09-10 | 22:33 | 2024-09-11 | 1:35 | 0.80104 | 0.0044013 | 78 | 182 | Planned | Planned interruption | Fleet plan - RMU 680 maintenance
57 |  | 95496-95496 | 995 Gore E Of Shannon | ELIN | Ocean Beach BFE 2 | 2024-09-13 | 13:36 | 2024-09-13 | 13:53 | 0.10552 | 0.006207 | 110 | 17 | Unplanned | Other cause | Allow high load to pass - High load
58 |  | 95505-95505 | Leven St 11 | ELIN | Leven St 11 LEV 11 | 2024-09-14 | 8:00 | 2024-09-14 | 12:44 | 0.016025 | 5.6427e-05 | 1 | 284 | Unplanned | Other cause | 5 Yearly maintenance - Service transformer & testing
59 |  | 95509-95509 | Do 15854 | ELIN | Leven St 9 LEV 9 | 2024-09-15 | 8:14 | 2024-09-15 | 12:04 | 0.10383 | 0.00045142 | 8 | 230 | Planned | Planned interruption | Fleet plan - Transformer maintenance
60 |  | 95624-95624 | Southern 8 | ELIN | Southern 8 SOU 8 | 2024-09-25 | 18:00 | 2024-09-25 | 19:36 | 0.027085 | 0.00028214 | 5 | 96 | Unplanned | Other cause | Upgrade - To replace LV fuseway
61 |  | 95642-95642 | 174/2 Liffey S Of Thames(2) | ELIN | Leven St 12 LEV 12 | 2024-09-29 | 6:00 | 2024-09-29 | 8:28 | 0.016702 | 0.00011285 | 2 | 148 | Planned | Planned interruption | Upgrade - RMU Maintenance
62 |  | 95667-95667 | 995 Gore E Of Shannon | ELIN | Ocean Beach BFE 2 | 2024-10-02 | 9:05 | 2024-10-02 | 15:24 | 2.3524 | 0.006207 | 110 | 379 | Planned | Planned interruption | Upgrade - Replace poles, crossarms & insulators
63 |  | 95715-95715 | 824/3 Rockdale Rd North Of Tweed | ELIN | Racecourse Rd 6 RRD 6 | 2024-10-08 | 8:09 | 2024-10-08 | 15:30 | 0.024884 | 5.6427e-05 | 1 | 441 | Planned | Planned interruption | Upgrade - Transformer maintenance
64 |  | 95718-95718 | 507/5 Conon S Of Tay | ELIN | Spey St 9 SPY 9 | 2024-10-08 | 8:15 | 2024-10-08 | 10:43 | 0.0083512 | 5.6427e-05 | 1 | 148 | Planned | Planned interruption | Upgrade - Transformer maintenance
65 |  | 95721-95721 | 995 Gore E Of Shannon | ELIN | Ocean Beach BFE 2 | 2024-10-08 | 19:10 | 2024-10-08 | 21:14 | 0.76966 | 0.006207 | 110 | 124 | Unplanned | Defective equipment | Deterioration - Damaged wires
66 |  | 95746-95746 | 398/2 Anglem At Museum | ELIN | Southern 8 SOU 8 | 2024-10-10 | 17:37 | 2024-10-10 | 19:43 | 0.01422 | 0.00011285 | 2 | 126 | Planned | Planned interruption | Upgrade - RMU maintenance
67 |  | 95895-95895 | 974 Barrow E. Of Palmer (974) | ELIN | Ocean Beach BFE 2 | 2024-10-26 | 17:46 | 2024-10-27 | 3:01 | 0.78293 | 0.0014107 | 25 | 555 | Unplanned | Defective equipment | Deterioration - Broken pole
68 |  | 95895-95895 | Gore St Cb | ELIN | Ocean Beach BFE 2 | 2024-10-26 | 17:46 | 2024-10-26 | 19:08 | 0.27299 | 0.0033292 | 59 | 82 | Unplanned | Defective equipment | Deterioration - Broken pole
69 |  | 96134-96134 | Spey St 9 | ELIN | Spey St 9 SPY 9 | 2024-11-21 | 9:28 | 2024-11-21 | 12:20 | 0.019411 | 0.00011285 | 2 | 172 | Unplanned | Unknown | Unknown - Blown fuses
70 |  | 96239-96239 | Spey St 9 | ELIN | Spey St 9 SPY 9 | 2024-11-30 | 6:58 | 2024-11-30 | 14:02 | 0.04785 | 0.00011285 | 2 | 424 | Unplanned | Other cause | Upgrade - New RMU
71 |  | 96381-96381 | Leven St 13 | ELIN | Leven St 13 LEV 13 | 2024-12-08 | 7:00 | 2024-12-08 | 11:33 | 0.30809 | 0.0011285 | 20 | 273 | Planned | Planned interruption | Upgrade - RMU maintenance
72 |  | 96361-96361 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2024-12-09 | 1:05 | 2024-12-09 | 1:29 | 0.0040627 | 0.00016928 | 3 | 24 | Unplanned | Adverse weather | High winds - Failed lead
73 |  | 96383-96383 | Spey St 11 | ELIN | Spey St 11 SPY 11 | 2024-12-09 | 9:33 | 2024-12-09 | 10:08 | 2.3522 | 0.067205 | 1191 | 35 | Unplanned | Defective equipment | Deterioration - Failed cable "GV"
74 |  | 96383-96383 | 685/2 Bourke E Of Windsor | ELIN | Spey St 11 SPY 11 | 2024-12-09 | 9:33 | 2024-12-09 | 10:18 | 0.42151 | 0.0093669 | 166 | 45 | Unplanned | Defective equipment | Deterioration - Failed cable "GV"
75 |  | 96606-96606 | Shannon St S Of Gore St | ELIN | Bluff Borough BFE 1 | 2024-12-20 | 15:56 | 2024-12-20 | 18:37 | 1.8079 | 0.011229 | 199 | 161 | Unplanned | Defective equipment | Deterioration - Broken wire
76 |  | 96606-96606 | 961 Bann W Of Liffey | ELIN | Bluff Borough BFE 1 | 2024-12-20 | 15:56 | 2024-12-20 | 17:08 | 0.86537 | 0.012019 | 213 | 72 | Unplanned | Defective equipment | Deterioration - Broken wire
77 |  | 96606-96606 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2024-12-20 | 15:56 | 2024-12-20 | 17:00 | 0.27807 | 0.0043449 | 77 | 64 | Unplanned | Defective equipment | Deterioration - Broken wire
78 |  | 96606-96606 | Bann St Cb Bann St Cb | ELIN | Bluff Borough BFE 1 | 2024-12-20 | 15:56 | 2024-12-20 | 16:00 | 0.082158 | 0.020539 | 364 | 4 | Unplanned | Defective equipment | Deterioration - Broken wire
79 |  | 96658-96658 | 397/1 Surry Park (1) | ELIN | Spey St 11 SPY 11 | 2025-01-12 | 7:00 | 2025-01-12 | 9:51 | 0.09649 | 0.00056427 | 10 | 171 | Planned | Planned interruption | Upgrade - RMU 397 maintenance
80 |  | 96715-96715 | Do 37376 | ELIN | Leven St 9 LEV 9 | 2025-01-19 | 7:00 | 2025-01-19 | 10:04 | 0.010383 | 5.6427e-05 | 1 | 184 | Unplanned | Other cause | Upgrade - Replace transformer
81 |  | 96765-96765 | 585/2 Deveron N Of Don | ELIN | Spey St 12 SPY 12 | 2025-01-23 | 9:50 | 2025-01-23 | 10:02 | 0.050784 | 0.004232 | 75 | 12 | Unplanned | Defective equipment | Deterioration - Failed Halo RMU
82 |  | 96765-96766 | Leven St 6 | ELIN | Leven St 6 LEV 6 | 2025-01-23 | 9:50 | 2025-01-23 | 10:02 | 0.03521 | 0.0029342 | 52 | 12 | Unplanned | Defective equipment | Deterioration - Failed Halo RMU
83 |  | 96782-96782 | Southern 9 | ELIN | Southern 9 SOU 9 | 2025-01-24 | 17:31 | 2025-01-24 | 18:16 | 1.6987 | 0.03775 | 669 | 45 | Unplanned | Third party interference | Third party vehicle - Broken poles
84 |  | 96782-96782 | Southern 9 | ELIN | Southern 9 SOU 9 | 2025-01-24 | 17:31 | 2025-01-25 | 8:34 | 0.20381 | 0.00022571 | 4 | 903 | Unplanned | Third party interference | Third party vehicle - Broken poles
85 |  | 96782-96782 | 357/4 Otepuni At Lindisfarne (4) | ELIN | Southern 9 SOU 9 | 2025-01-24 | 17:31 | 2025-01-25 | 2:33 | 0.48934 | 0.00090283 | 16 | 542 | Unplanned | Third party interference | Third party vehicle - Broken poles
86 |  | 96917-96917 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2025-02-10 | 16:01 | 2025-02-10 | 16:30 | 0.0049092 | 0.00016928 | 3 | 29 | Unplanned | Defective equipment | Deterioration - Failed lead
87 |  | 96945-96945 | Bann St Cb Bann St Cb | ELIN | Bluff Borough BFE 1 | 2025-02-12 | 17:28 | 2025-02-12 | 17:59 | 0.63672 | 0.020539 | 364 | 31 | Unplanned | Third party interference | Safety isolation - Broken wires (telecom)
88 |  | 96981-96981 | 712/4 Janet W Of Elles Road | ELIN | Southern 10 SOU 10 | 2025-02-16 | 23:00 | 2025-02-17 | 2:53 | 1.0649 | 0.0045706 | 81 | 233 | Planned | Planned interruption | Upgrade - RMU & transformer maintenance
89 |  | 96998-96998 | 995 Gore E Of Shannon | ELIN | Ocean Beach BFE 2 | 2025-02-18 | 11:18 | 2025-02-18 | 11:34 | 0.099312 | 0.006207 | 110 | 16 | Unplanned | Other cause | Safety isolation - Allow high load to pass
90 |  | 97138-97138 | 170/1 Victoria Av Opp Thomson | ELIN | Spey St 6 SPY 6 | 2025-03-02 | 7:00 | 2025-03-02 | 11:03 | 1.2066 | 0.0049656 | 88 | 243 | Planned | Planned interruption | Upgrade - RMU maintenance
91 |  | 97287-97287 | Leven St 11 | ELIN | Leven St 11 LEV 11 | 2025-03-17 | 21:12 | 2025-03-17 | 22:08 | 1.8865 | 0.033687 | 597 | 56 | Unplanned | Third party interference | Third party vehicle - Car hit RMU/transformer 225
92 |  | 97287-97287 | Leven St 11 | ELIN | Leven St 11 LEV 11 | 2025-03-17 | 21:12 | 2025-03-18 | 1:15 | 1.1518 | 0.0047399 | 84 | 243 | Unplanned | Third party interference | Third party vehicle - Car hit RMU/transformer 225
93 |  | ¹ Extend table as necessary to disclose information for all individual interruptions