## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Electricity Invercargill Limited
| Disclosure Date | 2026-08-31
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 2 June 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Non-material) Amendment Determination 2026 [2026] NZCC 21.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012, as amended.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Electricity Invercargill Limited
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | 97425-97425 | 992 The Big Oyster | ELIN | Bluff Borough BFE 1 | 2025-04-03 | 9:20 | 2025-04-03 | 11:21 | 0.12251 | 0.0010125 | 18 | 121 | Planned | Planned interruption | Upgrade - Replace links
10 |  | 97463-97463 | 412/2 Bond S Of Victoria East (2) | ELIN | Lev 13 | 2025-04-08 | 9:33 | 2025-04-08 | 11:48 | 0.3645 | 0.0027 | 48 | 135 | Unplanned | Wildlife | Bird strike - Broken wires
11 |  | 97463-97463 | 436 Mersey At Spey | ELIN | Lev 13 | 2025-04-08 | 9:33 | 2025-04-08 | 12:03 | 0.28687 | 0.0019125 | 34 | 150 | Unplanned | Wildlife | Bird strike - Broken wires
12 |  | 97463-97463 | 449 Ettrick W. Of Mersey (449). | ELIN | Lev 13 | 2025-04-08 | 9:33 | 2025-04-08 | 13:20 | 0.28091 | 0.0012375 | 22 | 227 | Unplanned | Wildlife | Bird strike - Broken wires
13 |  | 97463-97463 | Leven St 10 | ELIN | Lev 10 | 2025-04-08 | 9:33 | 2025-04-08 | 10:05 | 0.3582 | 0.011194 | 199 | 32 | Unplanned | Wildlife | Bird strike - Broken wires
14 |  | 97463-97463 | Leven St 11 | ELIN | Lev 11 | 2025-04-08 | 9:33 | 2025-04-08 | 10:05 | 1.224 | 0.03825 | 680 | 32 | Unplanned | Wildlife | Bird strike - Broken wires
15 |  | 97463-97463 | Leven St 12 | ELIN | Lev 12 | 2025-04-08 | 9:33 | 2025-04-08 | 10:05 | 1.0062 | 0.031443 | 559 | 32 | Unplanned | Wildlife | Bird strike - Broken wires
16 |  | 97463-97463 | 492 Reserve W Of Bond (492) | ELIN | Lev 13 | 2025-04-08 | 9:33 | 2025-04-08 | 10:14 | 0.011531 | 0.00028125 | 5 | 41 | Unplanned | Wildlife | Bird strike - Broken wires
17 |  | 97463-97463 | 162/2 Victoria Ave At Prison (2) | ELIN | Lev 13 | 2025-04-08 | 9:33 | 2025-04-08 | 11:42 | 0.079818 | 0.00061874 | 11 | 129 | Unplanned | Wildlife | Bird strike - Broken wires
18 |  | 97463-97463 | 410 Mersey N Of Bute | ELIN | Lev 13 | 2025-04-08 | 9:33 | 2025-04-08 | 12:15 | 0.17314 | 0.0010687 | 19 | 162 | Unplanned | Wildlife | Bird strike - Broken wires
19 |  | 97726-97726 | 304/4 Conway/Trent Reserve | ELIN | Racecourse Rd 8 RRD 8 | 2025-05-14 | 11:36 | 2025-05-14 | 11:42 | 0.0351 | 0.0058499 | 104 | 6 | Unplanned | Other cause | Overload - Blown fuse
20 |  | 97726-97726 | Racecourse Rd 8 | ELIN | Racecourse Rd 8 RRD 8 | 2025-05-14 | 11:36 | 2025-05-14 | 11:39 | 0.072224 | 0.024075 | 428 | 3 | Unplanned | Other cause | Overload - Blown fuse
21 |  | 97726-97726 | 322/1 Lithgow N Of Lithgow Place | ELIN | Racecourse Rd 8 RRD 8 | 2025-05-14 | 11:36 | 2025-05-14 | 11:42 | 0.13939 | 0.023231 | 413 | 6 | Unplanned | Other cause | Overload - Blown fuse
22 |  | 97804-97804 | Shannon St S Of Gore St | ELIN | Bluff Borough BFE 1 | 2025-05-26 | 9:02 | 2025-05-26 | 12:45 | 2.5087 | 0.01125 | 200 | 223 | Planned | Planned interruption | Upgrade - Replace wire
23 |  | 97869-97869 | 412/2 Bond S Of Victoria East (2) | ELIN | Leven St 13 LEV 13 | 2025-05-31 | 3:27 | 2025-05-31 | 7:59 | 0.48959 | 0.0018 | 32 | 272 | Unplanned | Adverse weather | High winds - Failed insulator
24 |  | 97869-97869 | 436 Mersey At Spey | ELIN | Leven St 13 LEV 13 | 2025-05-31 | 3:27 | 2025-05-31 | 8:06 | 1.177 | 0.0042187 | 75 | 279 | Unplanned | Adverse weather | High winds - Failed insulator
25 |  | 97869-97869 | 404 Bond Pl. W. Of Mersey (404). | ELIN | Leven St 13 LEV 13 | 2025-05-31 | 3:27 | 2025-05-31 | 12:24 | 0.5135 | 0.00095624 | 17 | 537 | Unplanned | Adverse weather | High winds - Failed insulator
26 |  | 97869-97869 | Leven St 13 | ELIN | Leven St 13 LEV 13 | 2025-05-31 | 3:27 | 2025-05-31 | 7:13 | 1.0551 | 0.0046687 | 83 | 226 | Unplanned | Adverse weather | High winds - Failed insulator
27 |  | 97869-97869 | 489/2 Airport Ave N Of Stead (2) | ELIN | Leven St 13 LEV 13 | 2025-05-31 | 3:27 | 2025-05-31 | 3:41 | 0.0039375 | 0.00028125 | 5 | 14 | Unplanned | Adverse weather | High winds - Failed insulator
28 |  | 97927-97927 | 974 Barrow E. Of Palmer (974) | ELIN | Ocean Beach BFE 2 | 2025-06-03 | 13:08 | 2025-06-03 | 15:03 | 0.16172 | 0.0014062 | 25 | 115 | Unplanned | Defective equipment | Deterioration - Damaged wire
29 |  | 98214-98214 | 624/1 Ure S Of Bourke | ELIN | Racecourse Rd 9 RRD 9 | 2025-07-08 | 8:31 | 2025-07-08 | 15:02 | 1.8475 | 0.0047249 | 84 | 391 | Planned | Planned interruption | Upgrade - Replace transformer
30 |  | 98265-98265 | 718/3 Earn W Of Princess | ELIN | Southern 7 SOU 7 | 2025-07-15 | 11:00 | 2025-07-15 | 15:50 | 1.2724 | 0.0043874 | 78 | 290 | Planned | Planned interruption | Upgrade - RMU 718 maintenance
31 |  | 98344-98344 | Foyle W. Of Palmer | ELIN | Bfe 1 (Bnn) | 2025-07-25 | 2:09 | 2025-07-25 | 3:21 | 1.462 | 0.020306 | 361 | 72 | Unplanned | Defective equipment | Deterioration - Failed lead
32 |  | 98344-98344 | Gore St Cb | ELIN | Bfe 2 (Grs) | 2025-07-25 | 2:09 | 2025-07-25 | 3:21 | 0.34425 | 0.0047812 | 85 | 72 | Unplanned | Defective equipment | Deterioration - Failed lead
33 |  | 98344-98344 | Bann St Cb Bann St Cb | ELIN | Bfe 1 (Bnn) | 2025-07-25 | 2:09 | 2025-07-25 | 2:56 | 0.018506 | 0.00039375 | 7 | 47 | Unplanned | Defective equipment | Deterioration - Failed lead
34 |  | 98344-98344 | Ocean Beach | ELIN | Bfe 2 | 2025-07-25 | 2:09 | 2025-07-25 | 3:09 | 0.003375 | 5.6249e-05 | 1 | 60 | Unplanned | Defective equipment | Deterioration - Failed lead
35 |  | 98344-98344 | 995 Gore E Of Shannon | ELIN | Bfe 2 | 2025-07-25 | 2:09 | 2025-07-25 | 5:34 | 1.2684 | 0.0061874 | 110 | 205 | Unplanned | Defective equipment | Deterioration - Failed lead
36 |  | 98355-98355 | Bluff Borough | ELIN | Bluff Borough BFE 1 | 2025-07-26 | 9:31 | 2025-07-26 | 12:20 | 0.33271 | 0.0019687 | 35 | 169 | Unplanned | Defective equipment | Deterioration - Replace switch
37 |  | 98355-98355 | Bann St Cb Bann St Cb | ELIN | Bluff Borough BFE 1 | 2025-07-26 | 12:15 | 2025-07-26 | 12:20 | 0.093655 | 0.018731 | 333 | 5 | Unplanned | Defective equipment | Deterioration - Replace switch
38 |  | 98624-98624 | Leven St 9 | ELIN | Leven St 9 LEV 9 | 2025-08-28 | 11:23 | 2025-08-28 | 12:00 | 0.0041624 | 0.0001125 | 2 | 37 | Unplanned | Defective equipment | Deterioration - Failed cable
39 |  | 98624-98624 | Do 15845 | ELIN | Leven St 9 LEV 9 | 2025-08-28 | 11:23 | 2025-08-30 | 13:25 | 0.16886 | 5.6249e-05 | 1 | 3002 | Unplanned | Defective equipment | Deterioration - Failed cable
40 |  | 98620-98620 | 621/1 Fern S Of Talbot | ELIN | Racecourse Rd 12 RRD 12 | 2025-09-02 | 9:04 | 2025-09-02 | 14:48 | 2.3607 | 0.0068624 | 122 | 344 | Planned | Planned interruption | Upgrade - RMU maintenance
41 |  | 98617-98617 | 177/3 Winter Gardens (3) | ELIN | Spey St 7 SPY 7 | 2025-09-02 | 10:09 | 2025-09-02 | 13:30 | 0.022612 | 0.0001125 | 2 | 201 | Unplanned | Unknown | Deterioration - Failed fuses (lv)
42 |  | 98719-98719 | 118/2 Kelvin S Of Herbert (2) | ELIN | Spey St 6 SPY 6 | 2025-09-08 | 8:47 | 2025-09-08 | 13:54 | 0.77708 | 0.0025312 | 45 | 307 | Planned | Planned interruption | Maintenance - RMU Maintenance
43 |  | 98719-98719 | 118/5 Kelvin S Of Herbert (5) | ELIN | Spey St 6 SPY 6 | 2025-09-08 | 8:47 | 2025-09-08 | 13:57 | 0.81955 | 0.0026437 | 47 | 310 | Planned | Planned interruption | Maintenance - RMU Maintenance
44 |  | 99017-99017 | 431/1 Sth Construction Co Bond St | ELIN | Leven St 9 LEV 9 | 2025-09-28 | 8:00 | 2025-09-28 | 10:58 | 0.030037 | 0.00016875 | 3 | 178 | Planned | Planned interruption | Upgrade - RMU maintenance
45 |  | 99024-99024 | Southern 8 | ELIN | Southern 8 SOU 8 | 2025-09-29 | 8:24 | 2025-09-29 | 10:37 | 0.0074812 | 5.6249e-05 | 1 | 133 | Unplanned | Other cause | Upgrade - Decommision transformer
46 |  | 99080-99080 | 962 Bann E Of Liffey 962 | ELIN | Bluff Borough BFE 1 | 2025-10-03 | 9:32 | 2025-10-03 | 13:40 | 1.7019 | 0.0068624 | 122 | 248 | Planned | Planned interruption | Upgrade - CB maintenance
47 |  | 99143-99143 | Do 16025 | ELIN | Ocean Beach BFE 2 | 2025-10-09 | 8:45 | 2025-10-09 | 9:52 | 0.011306 | 0.00016875 | 3 | 67 | Planned | Planned interruption | Upgrade - Replace tramsformer
48 |  | 99189-99189 | Do 14529 | ELIN | Bluff Borough BFE 1 | 2025-10-11 | 14:16 | 2025-10-11 | 15:54 | 0.099224 | 0.0010125 | 18 | 98 | Unplanned | Unknown | Unknown - Blown fuses
49 |  | 99219-99219 | 361/1 Mitchell W Of Lindisfarne | ELIN | Spey St 5 SPY 5 | 2025-10-14 | 8:30 | 2025-10-14 | 13:10 | 2.7405 | 0.0097874 | 174 | 280 | Planned | Planned interruption | Upgrade - RMU maintenance
50 |  | 99226-99226 | 335/1 Racecourse Rd. Carnavon R.O.W | ELIN | Racecourse Rd 8 RRD 8 | 2025-10-15 | 12:43 | 2025-10-15 | 14:07 | 0.49612 | 0.0059062 | 105 | 84 | Unplanned | Defective equipment | Deterioration - Failed cable
51 |  | 99226-99226 | 304/2 Conway/Trent Reserve | ELIN | Racecourse Rd 8 RRD 8 | 2025-10-15 | 12:43 | 2025-10-15 | 13:44 | 0.54213 | 0.0088874 | 158 | 61 | Unplanned | Defective equipment | Deterioration - Failed cable
52 |  | 99226-99226 | 304/3 Conway/Trent Reserve | ELIN | Racecourse Rd 8 RRD 8 | 2025-10-15 | 12:43 | 2025-10-15 | 14:23 | 0.37687 | 0.0037687 | 67 | 100 | Unplanned | Defective equipment | Deterioration - Failed cable
53 |  | 99226-99226 | Racecourse Rd 8 | ELIN | Racecourse Rd 8 RRD 8 | 2025-10-15 | 12:43 | 2025-10-15 | 13:23 | 0.81674 | 0.020418 | 363 | 40 | Unplanned | Defective equipment | Deterioration - Failed cable
54 |  | 99226-99226 | 371/4 Tay W Of Stuart (4) | ELIN | Racecourse Rd 8 RRD 8 | 2025-10-15 | 12:43 | 2025-10-15 | 13:03 | 0.2835 | 0.014175 | 252 | 20 | Unplanned | Defective equipment | Deterioration - Failed cable
55 |  | 99236-99236 | Do 128652 | ELIN | Bluff Borough BFE 1 | 2025-10-16 | 8:30 | 2025-10-16 | 9:03 | 0.012994 | 0.00039375 | 7 | 33 | Unplanned | Defective equipment | Deterioration - Blown fuse
56 |  | 99447-99447 | Spey St 14 | ELIN | Spey St 14 SPY 14 | 2025-10-30 | 8:03 | 2025-10-31 | 17:18 | 0.11222 | 5.6249e-05 | 1 | 1995 | Unplanned | Defective equipment | Faulty U/G cable - Defective equipment
57 |  | 99514-99514 | Spey St 14 | ELIN | Spey St 14 SPY 14 | 2025-11-05 | 18:30 | 2025-11-05 | 23:05 | 0.030937 | 0.0001125 | 2 | 275 | Unplanned | Other cause | Upgrade - New RMU installation
58 |  | 99583-99583 | Bann St Cb Bann St Cb | ELIN | Bfe 1 (Bnn) | 2025-11-08 | 15:29 | 2025-11-08 | 16:20 | 1.0499 | 0.020587 | 366 | 51 | Unplanned | Defective equipment | Deterioration - Failed connection
59 |  | 99583-99583 | Bluff Borough | ELIN | Bfe 1 | 2025-11-08 | 15:29 | 2025-11-08 | 16:18 | 1.3533 | 0.027618 | 491 | 49 | Unplanned | Defective equipment | Deterioration - Failed connection
60 |  | 99583-99583 | Gore St Cb | ELIN | Bfe 2 (Grs) | 2025-11-08 | 15:29 | 2025-11-08 | 16:16 | 0.12425 | 0.0026437 | 47 | 47 | Unplanned | Defective equipment | Deterioration - Failed connection
61 |  | 99583-99583 | 974 Barrow E. Of Palmer (974) | ELIN | Bfe 2 (Grs) | 2025-11-08 | 15:29 | 2025-11-08 | 16:31 | 0.087186 | 0.0014062 | 25 | 62 | Unplanned | Defective equipment | Deterioration - Failed connection
62 |  | 99583-99583 | Do 620119 | ELIN | Bfe 2 (Grs) | 2025-11-08 | 15:29 | 2025-11-08 | 19:19 | 0.19406 | 0.00084374 | 15 | 230 | Unplanned | Defective equipment | Deterioration - Failed connection
63 |  | 99583-99583 | Gore St Cb | ELIN | Bfe 2 (Grs) | 2025-11-08 | 16:48 | 2025-11-08 | 19:19 | 0.0084936 | 5.6249e-05 | 1 | 151 | Unplanned | Defective equipment | Deterioration - Failed connection
64 |  | 99583-99583 | 912/2 Big Glory (2) | ELIN | Bfe 2 (Grs) | 2025-11-08 | 16:48 | 2025-11-08 | 17:08 | 0.001125 | 5.6249e-05 | 1 | 20 | Unplanned | Defective equipment | Deterioration - Failed connection
65 |  | 99583-99583 | Bluff Borough | ELIN | Bfe 1 | 2025-11-08 | 16:48 | 2025-11-08 | 17:08 | 0.55237 | 0.027618 | 491 | 20 | Unplanned | Defective equipment | Deterioration - Failed connection
66 |  | 99583-99583 | Bann St Cb Bann St Cb | ELIN | Bfe 1 (Bnn) | 2025-11-08 | 16:48 | 2025-11-08 | 17:14 | 0.53527 | 0.020587 | 366 | 26 | Unplanned | Defective equipment | Deterioration - Failed connection
67 |  | 99583-99583 | 973 Foreshore Rd | ELIN | Bfe 2 (Grs) | 2025-11-08 | 16:48 | 2025-11-08 | 17:14 | 0.10237 | 0.0039375 | 70 | 26 | Unplanned | Defective equipment | Deterioration - Failed connection
68 |  | 99583-99583 | Do 620119 | ELIN | Bfe 2 (Grs) | 2025-11-08 | 19:36 | 2025-11-08 | 19:39 | 0.0025312 | 0.00084374 | 15 | 3 | Unplanned | Defective equipment | Deterioration - Failed connection
69 |  | 100053-100053 | 814/3 Lime S Of Tweed (3) | ELIN | Southern 9 SOU 9 | 2025-11-23 | 4:27 | 2025-11-23 | 8:20 | 0.74705 | 0.0032062 | 57 | 233 | Unplanned | Defective equipment | Deterioration - Failed cable
70 |  | 100053-100053 | Southern 9 | ELIN | Southern 9 SOU 9 | 2025-11-23 | 4:27 | 2025-11-23 | 5:01 | 1.2068 | 0.035493 | 631 | 34 | Unplanned | Defective equipment | Deterioration - Failed cable
71 |  | 100382-100382 | Spey St 8 | ELIN | Spey St 8 SPY 8 | 2025-12-06 | 22:31 | 2025-12-07 | 1:05 | 4.6171 | 0.029981 | 533 | 154 | Unplanned | Unknown | Unknown - CB trip
72 |  | 100551-100551 | Leven St 13 | ELIN | Leven St 13 LEV 13 | 2025-12-14 | 6:30 | 2025-12-14 | 11:45 | 0.035437 | 0.0001125 | 2 | 315 | Unplanned | Other cause | Upgrade - Replace transformer
73 |  | 100607-100607 | Gore St (5) | ELIN | Bluff Borough BFE 1 | 2025-12-16 | 9:00 | 2025-12-16 | 14:29 | 3.7012 | 0.01125 | 200 | 329 | Planned | Planned interruption | Upgrade - Replace Poles
74 |  | 100650-100650 | 491 491 Cobbe S Of Stead | ELIN | Leven St 13 LEV 13 | 2025-12-17 | 9:28 | 2025-12-17 | 15:59 | 0.06598 | 0.00016875 | 3 | 391 | Unplanned | Other cause | Upgrade - Replace transformer
75 |  | 100660-100660 | Gore St Cb | ELIN | Ocean Beach BFE 2 | 2025-12-18 | 14:31 | 2025-12-18 | 15:12 | 0.039206 | 0.00095624 | 17 | 41 | Unplanned | Defective equipment | Failed tie wire - Wire off insulator
76 |  | 100691-100691 | 745/3 Martin At Nelson (3) | ELIN | Southern 10 SOU 10 | 2025-12-22 | 7:17 | 2025-12-22 | 8:30 | 0.13961 | 0.0019125 | 34 | 73 | Unplanned | Defective equipment | Deterioration - Failed cable "UQ"
77 |  | 100691-100691 | 745/3 Martin At Nelson (3) | ELIN | Southern 10 SOU 10 | 2025-12-22 | 7:17 | 2025-12-22 | 8:48 | 0.16892 | 0.0018562 | 33 | 91 | Unplanned | Defective equipment | Deterioration - Failed cable "UQ"
78 |  | 100691-100691 | 745/3 Martin At Nelson (3) | ELIN | Southern 10 SOU 10 | 2025-12-22 | 7:17 | 2025-12-22 | 9:03 | 0.1431 | 0.00135 | 24 | 106 | Unplanned | Defective equipment | Deterioration - Failed cable "UQ"
79 |  | 100842-100842 | 859/4 Freshbake Baker St (Cb4) | ELIN | Racecourse Rd 6 RRD 6 | 2026-01-05 | 15:24 | 2026-01-05 | 17:45 | 0.0079312 | 5.6249e-05 | 1 | 141 | Unplanned | Unknown | Unknown - Fire
80 |  | 100946-100946 | 260/3 Ness S Of Tyne(3) | ELIN | Spey St 14 SPY 14 | 2026-01-13 | 21:30 | 2026-01-13 | 23:24 | 0.032062 | 0.00028125 | 5 | 114 | Planned | Planned interruption | Routine service - RMU maintenance
81 |  | 101000-101000 | 961 Bann W Of Liffey | ELIN | Bluff Borough BFE 1 | 2026-01-20 | 10:00 | 2026-01-20 | 12:21 | 0.78518 | 0.0055687 | 99 | 141 | Planned | Planned interruption | Upgrade - Replace switch
82 |  | 101007-101007 | 350/3 At 88 Mary | ELIN | Spey St 5 SPY 5 | 2026-01-20 | 10:00 | 2026-01-20 | 14:16 | 0.95039 | 0.0037125 | 66 | 256 | Planned | Planned interruption | Routine service - Transformer testing
83 |  | 101211-101211 | 548/1 Jed N Of Yarrow | ELIN | Spey St 12 SPY 12 | 2026-02-07 | 21:25 | 2026-02-07 | 22:08 | 0.20075 | 0.0046687 | 83 | 43 | Unplanned | Defective equipment | Deterioration - Cable failure
84 |  | 101211-101211 | 585/1 Deveron N Of Don | ELIN | Spey St 12 SPY 12 | 2026-02-07 | 21:25 | 2026-02-07 | 22:32 | 0.015075 | 0.000225 | 4 | 67 | Unplanned | Defective equipment | Deterioration - Cable failure
85 |  | 101211-101211 | 519/1 Deveron S Of Spey (1) | ELIN | Spey St 12 SPY 12 | 2026-02-07 | 21:25 | 2026-02-07 | 21:38 | 0.091405 | 0.0070312 | 125 | 13 | Unplanned | Defective equipment | Deterioration - Cable failure
86 |  | 101211-101211 | Spey St 12 | ELIN | Spey St 12 SPY 12 | 2026-02-07 | 21:25 | 2026-02-07 | 22:28 | 0.24097 | 0.003825 | 68 | 63 | Unplanned | Defective equipment | Deterioration - Cable failure
87 |  | 101211-101212 | Leven St 10 | ELIN | Leven St 10 LEV 10 | 2026-02-07 | 21:25 | 2026-02-07 | 21:38 | 0.14625 | 0.01125 | 200 | 13 | Unplanned | Defective equipment | Deterioration - Cable failure
88 |  | 101215-101215 | Ocean Beach | ELIN | Ocean Beach BFE 2 | 2026-02-09 | 12:03 | 2026-02-09 | 12:56 | 0.068568 | 0.0012937 | 23 | 53 | Unplanned | Defective equipment | Deterioration - Repair leads
89 |  | 101250-101250 | Do 37382 | ELIN | Leven St 9 LEV 9 | 2026-02-13 | 10:37 | 2026-02-13 | 11:11 | 0.003825 | 0.0001125 | 2 | 34 | Unplanned | Defective equipment | Defective equipment - Broken conductor
90 |  | 101269-101269 | 819/5 Tweed @ Inglewood (5) | ELIN | Southern 8 SOU 8 | 2026-02-15 | 7:00 | 2026-02-15 | 13:43 | 2.2215 | 0.0055124 | 98 | 403 | Planned | Planned interruption | Routine maintenance - RMU service
91 |  | 101453-101453 | Do 14529 | ELIN | Bluff Borough BFE 1 | 2026-03-05 | 23:32 | 2026-03-05 | 23:53 | 0.021262 | 0.0010125 | 18 | 21 | Unplanned | Defective equipment | Deterioration - Failed connection
92 |  | 101538-101538 | 485/1 Victoria Ave E Of Mersey | ELIN | Leven St 13 LEV 13 | 2026-03-15 | 7:00 | 2026-03-15 | 14:02 | 1.9702 | 0.0046687 | 83 | 422 | Planned | Planned interruption | Maintenance - Maintenance
93 |  | 101609-101609 | Ocean Beach | ELIN | Ocean Beach BFE 2 | 2026-03-24 | 10:45 | 2026-03-24 | 11:38 | 0.0029812 | 5.6249e-05 | 1 | 53 | Unplanned | Defective equipment | Deterioration - Lead off
¹ Extend table as necessary to disclose information for all individual interruptions